# Reverse Osmosis Skid

Control & Operation Specification

EQSP32 Industrial IoT Controller

| Document | Detail |
| --- | --- |
| Title | Reverse Osmosis Skid - Control & Operation Specification |
| Revision | v0.3 (draft for review) |
| Date | 15 June 2026 |
| Controller | Erqos EQSP32 (single unit, on-board I/O only) |
| Prepared by | Erqos Technologies |
| Status | Draft - reflects sign-off changes (0-300 PSI sensors, TDS 10-min stop) |

# 1. Purpose & Scope

This document specifies the automatic control and operation of a single-pass reverse osmosis (RO) water-treatment skid driven by one Erqos EQSP32 controller using only its on-board I/O. It defines the I/O, sensor scaling, operating states, control sequence, process monitoring and protection, membrane-fouling detection, operator interface (run/stop and RGB status indicator) and fault handling.

Cloud connectivity, telemetry/MQTT, data logging, temperature compensation, PID control and a feed/booster pump are out of scope for this revision (see Section 12).

# 2. System Overview

Feed (brackish) water is gravity-fed from the supply tank(s) through a supply electro-valve and cartridge pre-filters to the suction of a fixed-speed high-pressure RO pump. The pump forces feed water across the RO membrane. Permeate (product water) flows to the clean-water tank; the concentrate (brine) leaves through a fixed flow restrictor that sets the membrane operating pressure and then to drain (waste).

A flush valve is plumbed in parallel with the flow restrictor on the brine line. With the flush valve closed the brine passes through the restrictor and the membrane is pressurised for production. With the flush valve open the brine bypasses the restrictor straight to drain, dropping the pressure and giving a high cross-flow forward-flush of the membrane surface (the pump keeps running during a flush).

Controlled actuators:

RO Pump - ON/OFF via a 24 V contactor coil (single speed).

Supply (inlet) valve - 24 V solenoid; opens feed to the pump.

Flush (brine-bypass) valve - 24 V solenoid; open = low-pressure forward-flush, closed = produce.

# 3. I/O Assignment

Channel numbers below are interpreted from the wiring diagram and should be confirmed against the final wiring.

| Terminal | Signal | Type | Function |
| --- | --- | --- | --- |
| ADIO1 | Pressure Meter IN | 4-20 mA in (CIN) | Membrane feed pressure (high-pressure side) |
| ADIO2 | Pressure Meter OUT | 4-20 mA in (CIN) | Membrane concentrate (brine) pressure |
| ADIO3 | Depth Meter - Clean Water Tank | 4-20 mA in (CIN) | Product tank level |
| ADIO4 | Depth Meter - Supply Tank | 4-20 mA in (CIN) | Feed tank level |
| ADIO5 | TDS Sensor IN | 0-5 V in (AIN) | Feed water TDS |
| ADIO6 | TDS Sensor OUT | 0-5 V in (AIN) | Permeate TDS |
| ADIO7 | Run/Stop selector | digital in (DIN) | Run enable / emergency stop / fault reset |
| ADIO8 | 10K NTC | NTC in (TIN) | RO pump motor temperature |
| DIO9 | Flow Meter IN | pulse in (PCC) | Feed flow |
| DIO10 | Flow Meter OUT | pulse in (PCC) | Permeate flow |
| DIO11 | RGB LED - Red | output (POUT) | Status indicator |
| DIO12 | RGB LED - Green | output (POUT) | Status indicator |
| DIO13 | RGB LED - Blue | output (POUT) | Status indicator |
| DIO14 | Flush valve | output (POUT, 24 V) | Brine-bypass / forward-flush valve |
| DIO15 | RO Pump contactor | output (POUT, 24 V) | Pump motor ON/OFF |
| DIO16 | Supply valve | output (POUT, 24 V) | Feed inlet valve |

# 4. Sensor Scaling & Engineering Units

| Sensor | Electrical | Engineering scale | Notes |
| --- | --- | --- | --- |
| Depth - both tanks | 4-20 mA | 4 mA = 0.00 m, 20 mA = 5.00 m (0-500 cm) | Linear |
| Pressure IN / OUT | 4-20 mA | 4 mA = 0 PSI, 20 mA = 300 PSI | Range extended to 300 PSI |
| TDS IN | 0-5 V | 0 V = 0, 5 V = 10,000 mg/L | Feed salinity |
| TDS OUT | 0-5 V | 0 V = 0, 5 V = 1,000 mg/L | Permeate quality |
| Flow IN / OUT | pulse | 100 pulses = 1 L | Controller integrates to L/min |
| Motor temp | 10K NTC | Standard 10K NTC (Beta 3435, 10 k ref) | Default characteristic |

The pressure transmitters are now 0-300 PSI (20 mA = 300 PSI). This keeps the 150-200 PSI operating band comfortably mid-scale and, crucially, lets the controller read genuine over-200 PSI conditions for fouling detection (Section 8) and provides headroom for an over-pressure safety trip at 250 PSI.

# 5. Operating States

| State | Condition | Pump | Valves | RGB |
| --- | --- | --- | --- | --- |
| STOP (E-stop) | Run/Stop selector in STOP | OFF | Supply closed, Flush closed | OFF |
| STOPPED - Tank Full | Clean tank full | OFF | Closed | Blue solid |
| PAUSED - Supply Low | Supply tank below minimum | OFF | Closed | Blue blinking |
| STARTING | Permissives met; pressure settling | ON | Supply open, Flush closed | Green |
| RUNNING | Producing within spec | ON | Supply open, Flush closed | Green solid |
| FLUSHING | Periodic 5-min forward-flush | ON | Supply open, Flush open | Yellow solid |
| WARNING | Running but marginal | ON | Producing | Yellow flashing |
| FAULT | Latched error | OFF | Closed (safe) | Red |

# 6. Control Logic & Sequence of Operation

## 6.1 Run/Stop selector (emergency stop & reset)

A maintained Run/Stop selector is the master enable and emergency stop.

STOP: immediately de-energises all outputs (pump OFF, both valves closed). Unconditional safe stop, bypasses minimum on-time.

Moving to STOP also clears any latched fault.

RUN: the controller runs the automatic sequence subject to the start permissives.

## 6.2 Power-on behaviour

On power-up, if the selector is in RUN, the skid begins automatic operation immediately (no operator start action, no power-up flush).

If the selector is in STOP at power-up, the skid stays halted until set to RUN.

## 6.3 Start permissives (all must be true to start the pump)

Run/Stop selector = RUN; no latched fault.

Supply tank level >= 50 cm.

Clean-water tank level < restart threshold (380 cm).

Motor temperature < 80 deg C.

Minimum OFF-time (10 s) since the pump last stopped has elapsed.

## 6.4 Start sequence

Open the supply valve.

Start the RO pump (flush valve stays closed so the restrictor builds membrane pressure).

Settling window (25 s): production alarms (flow, recovery, pressure-band, TDS) are masked while pressure and flow stabilise. Safety items (motor temp, over-pressure, sensor fault, E-stop) remain active.

Enter RUNNING and begin evaluating all production monitors (Section 7).

## 6.5 Motor protection (anti short-cycle)

Minimum ON-time = 10 s before a non-safety stop (tank full, supply low) is allowed.

Minimum OFF-time = 10 s before the pump may restart.

Safety stops (E-stop and faults) act immediately and ignore the minimum ON-time.

## 6.6 Periodic membrane flush

After 60 minutes of continuous run time the controller performs a 5-minute forward-flush.

During flush: pump ON, supply valve open, flush valve open (brine bypasses the restrictor) - low pressure, high cross-flow. RGB = yellow solid.

On completion: close the flush valve, resume RUNNING and reset the run timer.

## 6.7 Normal stop - clean-water tank full (with hysteresis)

At 400 cm, stop production (after the minimum ON-time). RGB = blue solid.

Restart automatically when the level falls to 380 cm and permissives are met.

## 6.8 Supply-low pause (with hysteresis)

Below 50 cm, stop the pump and wait. RGB = blue blinking.

Resume automatically at 60 cm (and other permissives met).

# 7. Process Monitoring & Protection

Warnings and short-time trips use debounce timers to avoid nuisance reactions to transients.

| Parameter | Normal band | Warning | Trip / action |
| --- | --- | --- | --- |
| Feed flow (IN) | ~10 L/min (8-12) | Outside band | ~0 with pump ON > 10 s -> dry-run FAULT |
| Recovery (permeate / feed) | 10 - 30 % | Out of range | Sustained out of range -> WARNING |
| Permeate TDS (OUT) | < 200 mg/L | Rising toward 200 | > 200 mg/L for 10 min -> FAULT stop |
| Pressure IN | 150 - 200 PSI | > 200 (early fouling) | > 250 PSI -> over-pressure FAULT |
| Pressure OUT | 150 - 200 PSI | Drift | > 250 PSI -> over-pressure FAULT |
| Motor temperature | < 80 deg C | Approaching 80 | >= 80 deg C -> FAULT stop |
| Analog sensors (4-20 mA) | 4 - 20 mA | - | < ~3.5 mA = broken wire -> sensor FAULT |

# 8. Membrane Fouling Detection

With the 0-300 PSI transmitters the controller can now directly detect feed pressure above 200 PSI.

Cleaning-required indication: feed pressure > 200 PSI while permeate flow is low indicates a fouled/scaled membrane. This raises a maintenance warning (yellow fast blink).

High feed pressure (> 200 PSI) with otherwise normal flow raises an early-fouling warning (yellow slow blink).

Differential pressure (Pressure IN - Pressure OUT) can be trended as a secondary fouling indicator.

An over-pressure above 250 PSI is treated as a safety FAULT (immediate stop).

# 9. Status Indication (RGB LED)

Only one state is shown at a time. Priority, highest to lowest: STOP (off) -> Fault (red) -> Flushing (yellow solid) -> Warning (yellow flashing) -> Running (green) -> Supply low (blue blink) -> Tank full (blue solid).

| Indication | Meaning |
| --- | --- |
| Off | Run/Stop selector in STOP, or no power |
| Blue - solid | Stopped: clean-water tank full |
| Blue - blinking | Paused: supply tank low |
| Green - solid | Running normally / in spec |
| Yellow - solid | Flushing the membrane |
| Yellow - slow blink | Marginal: feed pressure high / low (early fouling) |
| Yellow - medium blink | Marginal: low/high flow or recovery out of band |
| Yellow - fast blink | Marginal: rising permeate TDS / membrane cleaning required |
| Red | Stopped on fault (see Section 10 blink codes) |

# 10. Fault Handling & Reset

On any fault: stop the pump immediately (bypassing minimum ON-time) and drive outputs to the safe state (pump OFF, both valves closed). The fault latches.

Reset: move the Run/Stop selector to STOP (clears the latched fault), then back to RUN to resume; the minimum OFF-time still applies before restart.

| Fault | Detection | Red code | Action |
| --- | --- | --- | --- |
| Motor over-temperature | NTC >= 80 deg C | 1 blink | Latched stop |
| Dry-run / no feed flow | Flow IN ~0 with pump ON > 10 s | 2 blinks | Latched stop |
| Permeate out of spec | TDS OUT > 200 mg/L for 10 min | 3 blinks | Latched stop |
| Over-pressure / pressure fault | Pressure IN/OUT > 250 PSI | 4 blinks | Latched stop |
| Sensor fault | 4-20 mA input < ~3.5 mA (broken wire) | 5 blinks | Latched stop |

# 11. Default Parameters / Setpoints

| Parameter | Value |
| --- | --- |
| Supply tank - minimum to run | 50 cm |
| Supply tank - resume level | 60 cm |
| Clean tank - full / stop | 400 cm |
| Clean tank - restart level | 380 cm |
| Operating pressure band (IN & OUT) | 150 - 200 PSI |
| Pressure transmitter range | 0 - 300 PSI (20 mA = 300 PSI) |
| Over-pressure safety trip | 250 PSI |
| Permeate TDS limit | 200 mg/L |
| Permeate TDS fault delay | 10 min sustained |
| Feed flow target / band | ~10 L/min (8 - 12) |
| Recovery target | 10 - 30 % |
| Motor temperature limit | 80 deg C (10K NTC) |
| Periodic flush interval | every 60 min of run time |
| Flush duration | 5 min |
| Minimum pump ON-time | 10 s |
| Minimum pump OFF-time | 10 s |
| Start settling window | 25 s |
| Dry-run grace time | 10 s |
| Power-on | auto-run if Run/Stop = RUN |

# 12. Out of Scope (this revision)

MQTT / cloud connectivity, telemetry and remote dashboards.

Data logging / historian.

Temperature compensation of flow / TDS.

PID or any closed-loop modulating control (pump is simple ON/OFF).

Start-up / power-up flush and permeate flush-to-drain at start.

Feed / booster pump (supply is gravity-fed).

# 13. Open Points to Confirm

Confirm the feed-flow target/band (~10 L/min, 8-12) and the meter K-factor (100 pulses/L).

Confirm the interpreted ADIO/DIO channel numbers against the final wiring.

Confirm that out-of-spec permeate (TDS > 200 for 10 min) should STOP the skid (no divert-to-drain valve fitted).

Confirm warning thresholds, yellow flash-rate mapping, and debounce times.

Confirm the 250 PSI over-pressure safety trip value.

Should the fouling 'cleaning required' state only warn, or escalate to a stop after a set time?